## Interface Requirements Electric
General Requirements | Authority Feeds | Building/Developer Lot | Service Sub Feeds (Power/Lighting/Lifts/Amenities/Etc) | Future/Spare Feeds | Tenancies | Solar
Data Recording Interval [seconds] | 5 | 5 | 900 | 900 | 900 | 900
Minimum Data to be Trended | Serial number | Serial number | Serial number | Serial number | Serial number | Serial number
| Current Phase Average Sliding Window Demand Delivered | Current Phase Average Sliding Window Demand Delivered | Current Phase Average Sliding Window Demand Delivered | Current Phase Average Sliding Window Demand Delivered | Active Energy Delivered | Current Phase Average Sliding Window Demand Delivered
| Apparent Power Sliding Window Demand Delivered+Received | Apparent Power Sliding Window Demand Delivered+Received | Reactive Energy Delivered | Reactive Energy Delivered | Current Phase Average | Reactive Energy Delivered
| Reactive Power Sliding Window Demand Delivered - Received | Reactive Power Sliding Window Demand Delivered - Received | Reactive Energy Received | Reactive Energy Received | Active Power | Reactive Energy Received
| Reactive Energy Delivered | Reactive Energy Delivered | Active Power Sliding Window Demand Delivered-Received | Active Power Sliding Window Demand Delivered-Received | Power Factor Signed | Active Power Sliding Window Demand Delivered-Received
| Active Power Sliding Window Demand Delivered-Received | Active Power Sliding Window Demand Delivered-Received | Active Energy Delivered | Active Energy Delivered | Average Voltage Line-to-Neutral | Active Energy Delivered
| Active Energy Delivered | Active Energy Delivered | Active Energy Received | Active Energy Received | Current Phase A | Active Energy Received
| Current Phase Average | Current Phase Average | Active Power | Active Power | Current Phase B | Active Power
| Power Factor Signed | Power Factor Signed | Current Phase A | Current Phase A | Current Phase C | Current Phase A
| Average Voltage Line-to-Neutral | Average Voltage Line-to-Neutral | Current Phase B | Current Phase B | Average Voltage Line-to-Line | Current Phase B
| Voltage Phases AN | Voltage Phases AN | Current Phase C | Current Phase C | Frequency | Current Phase C
| Voltage Phases BN | Voltage Phases BN | Active Power Phase A | Active Power Phase A |  | Active Power Phase A
| Voltage Phases CN | Voltage Phases CN | Active Power Phase B | Active Power Phase B |  | Active Power Phase B
| Current Phase A | Current Phase A | Active Power Phase C | Active Power Phase C |  | Active Power Phase C
| Current Phase B | Current Phase B | Apparent Power | Apparent Power |  | Apparent Power
| Current Phase C | Current Phase C | Active Energy Delivered Phase A | Active Energy Delivered Phase A |  | Active Energy Delivered Phase A
| Voltage Phases AB | Voltage Phases AB | Active Energy Delivered Phase B | Active Energy Delivered Phase B |  | Active Energy Delivered Phase B
| Voltage Phases BC | Voltage Phases BC | Active Energy Delivered Phase C | Active Energy Delivered Phase C |  | Active Energy Delivered Phase C
| Voltage Phases CA | Voltage Phases CA
| Average Voltage Line-to-Line | Average Voltage Line-to-Line
| Apparent Energy Delivered-Received | Apparent Energy Delivered-Received
| PQ | PQ
| Harmonics | Harmonics
Alarms | Large Sag/Swell boundaries TBC | Large Sag/Swell boundaries TBC | Energy Delivered = 0 | Energy Delivered > 0 | Energy Delivered = 0 | Energy Received = 0
| PQ Event | PQ Event | Energy Received > 0 | Energy Received > 0 | Energy Received > 0 | Energy Delivered > 0
| Energy Delivered = 0 | Energy Delivered = 0
| Energy Received > 0 | Energy Received > 0
Notes | Meter data must be available via PME and Avani | Meter data must be available via PME, Avani and Living Campus | Meter data must be available via PME and Avani | Meter data must be available via PME and Avani | Meter data must be available via PME and Avani | Meter data must be available via PME, Avani and Living Campus
Tenant statements must be configured for the applicable tenancy,
PreQualified Metering Provider | AIT (PME) | AIT (PME) | AIT (PME) | AIT (PME) | AIT (PME) | AIT (PME)
| Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus)
PreQualified Meter Models | Schneider PM8000 series | Schneider PM8000 series | Schneider PM5000 series | As per similar meters in the board | Schneider iEM series | PM3000 series
|  |  | Power tags (Only Use for Non-billable Metering) | Power tags (Only Use for Non-billable Metering) |  | Power tags (Only Use for Non-billable Metering)
PreQualified IP Gateways | Schneider PAS800L | Schneider PAS800L | Schneider PAS800L | Schneider PAS800L | Schneider PAS800L | Schneider PAS800L
PreApproved Protocol | Modbus | Modbus | Modbus | Modbus | Modbus | Modbus
Meter Descriptors
| Descriptor | Detail | Example
Standard Meter Descriptors | MainMeter |  | 500.MSB_01_0001_MainMeter
| Submains |  | 500.SWB_01_0001_Submains
| Lighting |  | 500.SWB_01_0001_Lighting
| Mechanical |  | 500.SWB_01_0001_Mechanical
| Power |  | 500.SWB_01_0001_Power
| Lift |  | 500.MSW_01_0001_Lift1
| Spare |  | 500.SWB_01_0001_Spare
| PV_Array |  | 500.SWB_01_0001_PV_Array
Custom
Custom Meter Descriptors | Tenant | Tenant descriptor to be advised by properties and incude room reference
| Riser/Chassis | Riser/Chassis descriptor to include suitable descriptor (e.g. east/west)
| Plant | Plant descriptor to include Boiler/Chiller/Generator/etc reference
| Essential | Essential/NonEssential descriptors
| Safety Services/FIP | Descriptor for specialist safety services
| Spare | Spare descriptor
| Specialist Area | Descriptor for specialist area (e.g. hotel, specialist lab, etc)
Network Connection Overview
Visualisation Requirements
PME | SLD/Meter Tree Topology
Visio/AutoCAD | Network Topology | See Visualisation Samples Tab
PME | Floorplan view | See Visualisation Samples Tab
Living Campus | Solar Page | To be included post-update in early 2024
| Building view | To be included post-update in early 2024
Plantroom Cooling view
Avani Portal | Points Listing
API Calls & Tags
Energy Benchmarking Dashbaords |  | To be discussed in line with energy groupings & portfolio views

## Interface Requirements Mech
Service Metered | Tenancies | Building/Developer Lot | Mechanical Plantroom
Data Recording Interval [minutes] | 300 | 300 | 300
Minimum Points Requirements | Thermal Energy | Thermal Energy | Thermal Energy
| Thermal Power | Thermal Power | Thermal Power
| Water Flow Rate | Water Flow Rate | Water Flow Rate
| Supply Temperature | Supply Temperature | Supply Temperature
| Return Temperature | Return Temperature | Return Temperature
Alarms | Water Flow Rate = 0 for extended period | Water Flow Rate = 0 for extended period | Water Flow Rate = 0 for extended period
| Supply Temperature not changing | Supply Temperature not changing | Supply Temperature not changing
| Return Temperature not changing | Return Temperature not changing | Return Temperature not changing
Notes | Thermal energy is only trended at 15 minute intervals. | Thermal energy is only trended at 15 minute intervals. | Thermal energy is only trended at 15 minute intervals.
| Virtual meter logic must be consistent across connected platforms | Virtual meter logic must be consistent across connected platforms | Virtual meter logic must be consistent across connected platforms
| Thermal Energy and Power are calculated values and must be calculated in the BacRouter, not the BMS. | Thermal Energy and Power are calculated values and must be calculated in the BacRouter, not the BMS. | Thermal Energy and Power are calculated values and must be calculated in the BacRouter, not the BMS.
COPs are calculated within the BMS and shared externally with other platforms.
Prequalified Metering Provider | Mizco (JCI BMS) | Mizco (JCI BMS) | Mizco (JCI BMS)
| Schneider (Ecostructure BMS) | Schneider (Ecostructure BMS) | Schneider (Ecostructure BMS)
| Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus)
Prequalified Meter Models | Siemens MAGFLOW | Siemens MAGFLOW | Siemens MAGFLOW
| Siemens MAGFLOW | Siemens MAGFLOW | Siemens MAGFLOW
Prequalified IP Routers | Intesis MS/TP to IP Router | Intesis MS/TP to IP Router | Intesis MS/TP to IP Router
PreApproved Protocol | BACnet & Modbus | BACnet & Modbus | BACnet & Modbus
Meter Descriptors
| Descriptor | Detail
Standard Meter Descriptors | MainMeter | Where multiple main meters exist for a building an additional descriptor may be required to distinguish
Custom
Custom Meter Descriptors | Tenant | Tenant descriptor to be advised by properties and incude room reference
| Specialist Area | Descriptor for specialist area (e.g. specialist lab, etc)
Network Connection Overview
Visualisation Requirements
BMS | Meter Tree Topology | See Visualisation Samples Tab
Visio/AutoCAD | Network Topology | See Visualisation Samples Tab
BMS | Floorplan view | See Visualisation Samples Tab
Living Campus | Building view | To be included post-update in early 2024
Plantroom Heating view
Plantroom Cooling view
Avani Portal | Points Listing
API Calls & Tags
Energy Benchmarking Dashbaords |  | To be discussed in line with energy groupings & portfolio views
Note on E18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Use Siemens Magflow meters only
Note on C38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Nothing in the sample tab

## Interface Requirements Hyd
| Water | [5 empty] | Gas
Service Metered | Authority Feeds | Tenancies | Building/Developer Lot | Mechanical Plantroom | Mech Services Meters: Cooling Towers/Top Up | Future/Spare | Authority Feeds | Tenancies | Building/Developer Lot | Future/Spare | Mechanical Plantroom
Data Sampling Interval [seconds] | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900
Minimum Points Requirements | Consumption/Volume/kL | Consumption/Volume/kL | Consumption/Volume/kL | Consumption/Volume/kL | Consumption/Volume/kL | Consumption/Volume/kL | Consumption/Volume/m3 | Consumption/Volume/m3 | Consumption/Volume/m3 | Consumption/Volume/m3 | Consumption/Volume/m3
Water Volume Flow Rate
Water Volume Flow Rate mean
Water Volume Flow Rate low
Water Volume Flow Rate high
Alarms | Consumption = 0 | Consumption = 0 | Consumption = 0 | Consumption = 0 | Consumption = 0 | Consumption>0 | Consumption = 0 | Consumption = 0 | Consumption = 0 | Consumption > 0 | Consumption = 0
Notes | Data retention for LoraWan battery powered loggers |  |  | Plantroom submetering to include makeup water and cooling tower water | [6 empty] | Plantroom submetering to include gas per boiler
Gateways will retain data.
Lorawan log and broadcast
Prequalified Metering Provider | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan) | TBC (Lorawan)
| TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired) | TBC (Hardwired)
| Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus) | Avani (Avani and Living Campus)
Prequalified Meter Models | Itron TD8 series (DN 20 to 32 mm, with current NMI approval) with disconnection unions | Itron TD8 series (DN 20 to 32 mm, with current NMI approval) with disconnection unions | Itron TD8 series (DN 20 to 32 mm, with current NMI approval) with disconnection unions | Itron TD8 series (DN 20 to 32 mm, with current NMI approval) with disconnection unions | Itron TD8 series (DN 20 to 32 mm, with current NMI approval) with disconnection unions | Itron TD8 series (DN 20 to 32 mm, with current NMI approval) with disconnection unions | Zenner Atmos G/WG | Zenner Atmos G/WG | Zenner Atmos G/WG | Zenner Atmos G/WG | Zenner Atmos G/WG
| Itron Flostar M series (DN 40 to 150 mm, with current NMI approval) with flanged connections | Itron Flostar M series (DN 40 to 150 mm, with current NMI approval) with flanged connections | Itron Flostar M series (DN 40 to 150 mm, with current NMI approval) with flanged connections | Itron Flostar M series (DN 40 to 150 mm, with current NMI approval) with flanged connections | Itron Flostar M series (DN 40 to 150 mm, with current NMI approval) with flanged connections | Itron Flostar M series (DN 40 to 150 mm, with current NMI approval) with flanged connections | FMG FMR G series | FMG FMR G series | FMG FMR G series | FMG FMR G series | FMG FMR G series
| Itron Woltex M (DN 200 mm and above) | Itron Woltex M (DN 200 mm and above) | Itron Woltex M (DN 200 mm and above) | Itron Woltex M (DN 200 mm and above) | Itron Woltex M (DN 200 mm and above) | Itron Woltex M (DN 200 mm and above)
Prequalified Logger Models | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0 | Itron M‐Bus Cyble v2.0
| Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN) | Milesight (LoRa WAN)
| Itron Cyble 5A logger | Itron Cyble 5A logger | Itron Cyble 5A logger | Itron Cyble 5A logger | Itron Cyble 5A logger | Itron Cyble 5A logger | LoRaWAN Smart Electronic Index | LoRaWAN Smart Electronic Index | LoRaWAN Smart Electronic Index | LoRaWAN Smart Electronic Index | LoRaWAN Smart Electronic Index
Prequalified Gateways | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet) | Intesis (MBus to BACnet)
| TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus) | TechBase (MBus to Modbus)
PreApproved Protocol | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus | MBus, BACnet & Modbus
Meter Descriptors
| Descriptor | Detail
Standard Water Meter Descriptors | MainMeter | Where multiple main meters exist for a building an additional descriptor may be required to distinguish
Amenities
Cleaners
Laundry
Kitchen
Custom
Custom Water Meter Descriptors | Tenant | Tenant descriptor to be advised by properties and incude room reference
| Mechanical | Mechanical MakeUp/Cooling Tower/Hot Water Plant
| Recycled | To include recycled collection/consumption points in the building and Recycled MakeUp from potable
| Irrigation | To be inlcuded where irrigation is fed from the building recycled or potable water systems
| Spare | Spare descriptor
| Specialist Area | Descriptor for specialist area (e.g. hotel, End of Trip, specialist lab, etc)
Standard Gas Meter Descriptors | MainMeter
Custom
Custom Gas Meter Descriptors | Tenant | Tenant descriptor to be advised by properties and incude room reference
| Mechanical | Boiler referecne to be included in the descriptor
| Specialist Area | Descriptor for specialist area (e.g. specialist lab, etc)
Network Connection Overview
Visualisation Requirements
BMS | Meter Tree Topology | See Visualisation Samples Tab
Visio/AutoCAD | Network Topology | See Visualisation Samples Tab
BMS | Floorplan view | See Visualisation Samples Tab
Living Campus | Building view | To be included post-update in early 2024
Plantroom Heating view
Plantroom Cooling view
Avani Portal | Points Listing
API Calls & Tags
Water Benchmarking Dashbaords |  | To be discussed in line with energy groupings & portfolio views

## Visualisation Samples
Meter Tree Sample | Network Topology Sample
Metering Floor Plan Sample
Mech Floor Plan Sample